READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - The extent and location of “Standalone Multipreset Modular Dimming Controls” Work is shown in the Contract Documents. This section includes:

    - Wall-box multi-scene dimming controls

    - Multipreset modular dimming controls.

Modular dimming control systems can be used in large conference rooms and in some public spaces where daylight dimming and occupancy based dimming and switching are desired. Dimming and switching of fixtures in public spaces with F&I approval.

Consider using digital dimming systems in areas where it may be desirable to reconfigure control zones in the future.

Coordinate compatibility of dimming system and controls with LED drivers used on project

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - IEEE PC62.41.1

    - IEEE PC62.41.2

    - NECA (National Electrical Contractors Association) - National Electrical Installation Standards

    - NFPA 70 (National Fire Protection Association) - National Electrical Code

    - Washington State Energy Code

    - UL 508

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data:

        - For modular dimming controls; include elevation, dimensions, features, characteristics, ratings, and labels.

        - Device plates and plate color and material.

        - LED drivers compatible with dimmers.

      - Shop Drawings:

        - Diagrams for power, signal, and control wiring.

        - Load schedule indicating actual connected load, load type and voltage per circuit and control zones.

      - Field quality control and test reports

      - Commissioning Plan with test procedures.

  - QUALITY ASSURANCE

    - Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

  - WARRANTY

    - Manufacturer's standard form in which manufacturer agrees to repair or replace components of dimming controls that fail in materials or workmanship within specified warranty period of two years.

- PRODUCTS

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Leviton Mfg. Company Inc.

      - Lutron Electronics

      - Crestron

      - Acuity

      - Or Approved Equal

  - GENERAL DIMMING DEVICE REQUIREMENTS

    - Compatibility:

      - Dimming control components shall be compatible with lighting fixtures, LED drivers, and transformers.

- Engineer to remove control methods not included in the project.

      - Dimming control devices shall be compatible with lighting control system components specified in Section 260943.13 "Addressable-Fixture Lighting Controls" and Section 260943.23 "Relay-Based Lighting Controls," and in Section 260923 "Lighting Control Devices."

    - Dimmers and Dimmer Modules: Comply with UL 508.

      - Audible Noise and Radio-Frequency Interference Suppression: Solid-state dimmers shall operate smoothly over their operating ranges without audible lamp or dimmer noise or radio-frequency interference. Modules shall include integral or external filters to suppress audible noise and radio-frequency interference.

      - Dimmer or Dimmer-Module Rating: Not less than 125 percent of connected load unless otherwise indicated.

    - Surge Protection: Withstand supply power surges without impairment to performance.

      - Panels: 6000 V, 3000 A, complying with IEEE PC62.41.1 and IEEE PC62.41.2.

      - Other System Devices: 6000 V, 3000 A, complying with IEEE PC62.41.1 and IEEE PC62.41.2.

    - Off Control Position: User-selected off position of any control point shall disconnect the load from line supply.

  - WALL-BOX MULTISCENE DIMMING CONTROLS

    - Description: Factory-fabricated equipment consisting of a wall-box-mounted master programmable controller and indicated number of wall-box zone stations. Controls and dimmers shall be integrated for mounting in multigang wall box under a single wall plate. Each zone shall be adjustable to indicated number of scenes, which shall reside in the memory of zone controller.

    - Each zone shall be configurable to control the following loads:

      - LED with 0-10V dimming driver.

      - Non-dim, on-off switching only.

    - Dimmers: Regulate voltages to maintain a constant light level, with no visible flicker, when the source voltage varies plus or minus 2 percent rms.

    - Memory:

      - Retain preset scenes and fade rates through momentary (up to 3-second) power interruptions.

      - Retain preset scenes through power failures for at least seven days.

    - Device Plates: Style, material, and color shall comply with Section 262726 "Wiring Devices." Master-control cover plate shall be one piece.

    - Master controller shall include the following:

      - Cover-mounted switches, including master off, all bright, and selectors for each scene.

      - Cover-mounted LED indicator lights, one associated with each scene switch, and one for the master off switch.

      - Concealed switches and indicators for specified function.

      - A raise/lower switch for each zone for temporary adjustments of the zone, without altering scene values stored in memory.

      - Fade time indicated by digital display for current scene while fading.

      - Cover-mounted infrared receiver.

    - Infrared Transmitters: Wireless remote control for recalling each of the presets. Operate up to 50 feet within line of sight of the master controller.

  - MULTIPRESET MODULAR DIMMING CONTROLS

    - Description: Factory-fabricated equipment providing manual dimming consisting of. the following:

      - Master controller.

      - Dimmer panels and indicated number of zone stations.

      - Controls and dimmers shall be integrated for mounting in a multigang wall box under a single wall plate.

      - Each zone shall be adjustable to indicated number of scenes, which shall reside in the memory of zone controller.

    - Each zone shall be configurable to control the following loads:

      - Non-dim, on-off switching only.

      - Neon and cold-cathode lighting.

      - LED with 0-10V dimming driver.

    - Dimmers: Regulate voltages to maintain a constant light level, with no visible flicker, when the source voltage varies plus or minus 2 percent rms.

    - Memory: Retain preset scenes and fade settings through power failures by retaining physical settings of controls.

    - Device Plates: Style, material, and color shall comply with Section 262726 "Wiring Devices." Master-control cover plate shall be one piece.

    - Master controller shall include the following:

      - Wall-box style, single cover plate supplied by manufacturer.

      - Cover-mounted switches, including master off, all bright, and selectors for each scene.

      - Cover-mounted LED indicator lights, one associated with each scene switch, and one for the master off switch.

      - Concealed switches and indicators for specified function.

      - A raise/lower switch for each zone for temporary adjustments of the zone, without altering scene values stored in memory.

      - Fade time indicated by digital display for current scene while fading.

      - Cover-mounted infrared receiver.

    - Remote-Control Stations:

      - Numbered push buttons to select scenes.

      - Off switch to turn all zones off.

      - Raise/lower to temporarily adjust all zones of light simultaneously in current scene.

      - Control Wiring: NFPA 70, Class 2.

      - Mounting: Single flush wall box with manufacturer's standard faceplate, color per Section 262726 “Wiring Devices”.

    - Dimmer Panels: Modular, plug-in type, complying with UL 508.

      - Integrated Short-Circuit Rating: Rated for available fault current.

      - Dimmers:

        - Dimming Circuit: Two SCR dimmers, in inverse parallel configuration.

        - Dimming Curve: Modified "square law" as specified in IESNA's "IESNA Lighting Handbook"; control voltage is 0- to 10-V dc.

        - Dimming Range: 10 to 100 percent, OR 1 to 100 percent where required by lighting design considerations. Full output voltage not less than 98 percent of line voltage.

        - Voltage Regulation: Dimmer shall maintain a constant light level, with no visible flicker, when the source voltage varies plus or minus 2 percent in rms voltage.

    - Circuit Breakers: Complying with UL 489 and classified as switch duty (SWD).

- EXECUTION

  - WIRING INSTALLATION

    - Comply with NECA 1.

    - Wiring to Supply Side of Remote-Control Power Sources: Comply with requirements in Section 260519 "600 Volt or Less Wire and Cable."

    - Class 2 Control Cable: Multiconductor cable with stranded-copper conductors sized per manufacturer’s recommendations.  Comply with requirements in Section 260523 "Control Signal Transmission Media."

    - Wiring Methods: Comply with Section 260533 “Raceways and Boxes”.

    - Wiring within Enclosures: Bundle, lace, and train conductors to terminal points. Separate power-limited and nonpower-limited conductors according to conductor manufacturer's written instructions.

  - IDENTIFICATION

    - Comply with requirements in Section 260553 "Identification for Electrical Systems" for identifying components and power and control wiring.

    - Label each dimmer module with a unique designation.

    - Label each scene control button with approved scene description.

  - FIELD QUALITY CONTROL

    - Manufacturer's Field Service: Where required by scope of project, engage a factory-authorized service representative to perform initial test and inspection of components, assemblies, and equipment installations, including connections.

    - Perform the following Tests and Inspections:

      - Continuity tests of circuits.

      - Operational Test: Set and operate controls to demonstrate their functions and capabilities in a methodical sequence that cues and reproduces actual operating functions.

        - Include testing of modular dimming control equipment under conditions that simulate actual operational conditions. Record control settings, operations, cues, and functional observations.

    - Remove and replace malfunctioning modular dimming control components and retest as specified above.

    - Test Labeling: After satisfactory completion of tests and inspections, apply a label to tested components indicating test results, date, and responsible agency and representative.

    - Reports: Written reports of tests and observations.

      - Record defective materials and workmanship.

      - Unsatisfactory test results.

      - Record repairs and adjustments.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain modular dimming controls.

- Remove sections listed below that are not included for the project.

    - Coordinate demonstration of products specified in this Section with demonstration requirements for low-voltage, programmable lighting control system specified in Section 260943.13 "Addressable-Fixture Lighting Controls" and Section 260943.23 "Relay-Based Lighting Controls."

  - COMMISSIONING

    - Provide controls commissioning according to Washington State Energy Code requirements.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

09/20/2021	New section